## Storage Tank Section
  denr.sd.gov/Tanks

Proposed UST rules           changes - 2018

This fact sheet describes the proposed UST rules changes for the regulated tanks.

# Walk-through inspections by owners/operators (Class A&B)

  - Starting October 2018:

    - Monthly - inspect the leak detection equipment and spill prevention equipment (buckets).

    - Annually - inspect the containment sumps.

# Spill prevention equipment tightness test every 3 years

  - Must be tested by October 2021 or have double-walled spill bucket with interstitial monitoring.

# Overfill prevention equipment inspection every 3 years

  - Must be tested by October 2021.

    - Ensures the equipment is set at the appropriate level.

    - Ensures the ball float is still in working condition. If not, then replace it with either automatic shut-off device or overfill alarm.

# Tightness test (every 3 years) for containment sumps used for piping leak detection

  - Must be tested by October 2021.

- Release detection requirements for emergency generator tanks

  - New tanks must have leak detection after October 2018.

  - Existing tanks must have leak detection by October 2021.

- Eliminates Ball-Float Valves as overfill protection

  - Existing ball-float valves are grandfathered in provided they are in working condition.

  - Must be tested by October 2021 to make sure they are in working condition.

# Starting October 2018

# Notification 30 days prior to switching to >10% ethanol or >20% biodiesel.

  - Test within 30 days after repair to spill or overfill equipment.

  - Change of Ownership Notification (DENR’s Change of Ownership Form).

- Removed past deferrals for field constructed tanks and airport hydrant systems; they must comply with the UST requirements by October 2021.